## Table 1
Alabama Department of Environmental Management Wastewater Treatment and Collection System Classification Worksheet for Operator Certification
Criteria for Classifying Wastewater Treatment Systems (ADEM Admin. Code R. 335-10-1-.06)
Fill out one form for each utility treatment plant and/or collection system as long as both are associated with the same permit number. Note: Shaded boxes are automatically calculated and do not require data entry. Do not enter information in shaded boxes.
Date:
Permitee:
Facility |  | Plant Name
NPDES #
Street Name
City/State/Zip
Plant/System Superintendent or Chief Operator Completing Form |  | Name
Title
Operator Number
Phone
Email
Narrative Description of Plant
Population Served By Collection System
Grade of Collection System |  |  | Grade IC
Grade of Treatment Plant based on ranking |  |  | Grade I
Collection System Classification |  |  |  | based on population
Grade IC |  |  |  | 1 to 15,000
Grade IIC |  |  |  | 15,001 or greater
WWT Classification |  |  |  | based on following point system
Grade I |  |  |  | 36 points or less
Grade II |  |  |  | 37 – 60 points
Grade III |  |  |  | 61 – 84 points
Grade IV |  |  |  | 85 points and greater
Item |  |  |  |  | Points | Your Plant | Can write notes or comments below:
Size (0 point minimum to 40 point maximum)
Population served (0 point minimum to 20 point maximum) |  |  |  |  | 1 pt per 10,000
Average daily design flow (0 point minimum to 20 point maximum) |  |  |  |  | 1 pt per MGD or part
Industrial or Hydraulic Loading Considerations
Influent subject to I/I that affects plant operation [See Note 1] |  |  |  |  | 2
“Categorical” industrial discharge or “major industrial wastewater discharge(s) (major means greater than 20% plant organic/nitrogenous domestic loading capacity or flow greater than 25,000 gpd) |  |  |  |  | 4
Impact of septage or truck-hauled waste (0 point minimum to 2 point maximum) – typical grease/solids concerns [See Note 1] |  |  |  |  | 0-2
Toxicity impacts affecting plant nitrification or other plant operational performance [See Note 1] |  |  |  |  | 4
Preliminary Treatment (Select all applicable items)
On-site plant lift station for influent flow to plant |  |  |  |  | 2
Non-Mechanical Simple Bar Screen |  |  |  |  | 0
Mechanical Screen with or without communition |  |  |  |  | 1
Hydroscreen – one or more |  |  |  |  | 1
Grit removal (gravity/cyclone) |  |  |  |  | 1
Grit removal (mechanical) with or without aeration |  |  |  |  | 2
Equalization Tank or Basin |  |  |  |  | 1
Microscreen/Filter Pretreatment (e.g., Salsnes solids removal or other filter) |  |  |  |  | 3
Pre-Treatment Lagoon tank, basin, or tank (one or more) |  |  |  |  | 5
Primary Treatment (Select all applicable items)
Primary Clarifier(s) |  |  |  |  | 5
Community Septic Tanks (STEP = 1, STEG = 0) |  |  |  |  | 1
Dissolved air flotation clarifier |  |  |  |  | 7
Microscreen/Filter Pretreatment (e.g., Salsnes solids removal or other filter) |  |  |  |  | 3
Chemical Addition Pre-Treatment System (lime/alkalinity, TP removal, metals removal). Add 2 points per reagent/chemical addition. |  |  |  |  | 2-6
Imhoff tanks or similar |  |  |  |  | 2
Grease Separator |  |  |  |  | 2
Dedicated Fats, Oils, and Grease (FOG) treatment system not otherwise specified |  |  |  |  | 7
Secondary Treatment (Select all applicable items)
Package Fixed-film/media reactor (e.g., Orenco system) or a package mechanical activated sludge plant with an avg daily design flow of less than 15,000 gpd |  |  |  |  | 5
Activated sludge (Conventional, Extended Air, Step-Feed, SBR, MBR, oxidation ditch, VLR, etc.) |  |  |  |  | 15
Stabilization lagoons (1 to or more cells without aeration) |  |  |  |  | 5
Stabilization lagoons (1 or more cells with partial mixing and/or partial aeration) |  |  |  |  | 7
Stabilization lagoons (1 or more cells with or complete mix and/or full aeration or total horsepower aeration of 100 hp or more) |  |  |  |  | 9
Trickling Filter or packed bed biofilter tower roughing treatment with or without recirc. |  |  |  |  | 7
Trickling Filter or packed bed biofilter tower secondary treatment |  |  |  |  | 10
Trickling Filter with solids contact system |  |  |  |  | 12
Pure oxygen activated sludge with or without oxygen generation |  |  |  |  | 20
Rotating biological contactors (1 to 4 shafts) |  |  |  |  | 7
Rotating biological contactors (5 or more shafts) |  |  |  |  | 12
Denitrification via activated sludge-on/off aeration or integral oxidation ditch anoxic zone |  |  |  |  | 2
Denitrification via separate stage anoxic activated sludge basin or tank with recycle |  |  |  |  | 4
Biological phosphorus removal with separate stage anaerobic activated sludge basin or tank with recycle |  |  |  |  | 8
Tertiary Treatment and/or Other Treatment Processes (Select all applicable items)
Mechanical Post-Aeration (≤ 5 hp) |  |  |  |  | 1
Mechanical Post-Aeration (> 5 hp or part of a combined diffused air system) |  |  |  |  | 2
Polishing ponds for advanced biological waste treatment |  |  |  |  | 2
Chemical/physical advanced waste treatment for tertiary metals/toxicant removal [includes all chemical addition, reaction basins, and filtration or solids handling) |  |  |  |  | 10
Activated sludge polishing treatment |  |  |  |  | 12
Ion exchange for advanced waste treatment |  |  |  |  | 10
Reverse osmosis, ultrafiltration, electrodialysis and other membrane filtration techniques |  |  |  |  | 15
Granular or Powdered Activated carbon advanced waste treatment |  |  |  |  | 4
Media Filtration (gravity/sand/multimedia/disk filter) |  |  |  |  | 3
Microscreen/Filter post-treatment if not addressed above |  |  |  |  | 3
Dissolved air flotation (for other than sludge thickening as part of solids handling below) |  |  |  |  | 8
Intermittent sand filter |  |  |  |  | 2
Continuous Recirculating intermittent sand filter |  |  |  |  | 4
Pressure filtration units |  |  |  |  | 4
Chemical addition for tertiary phosphorus removal |  |  |  |  | 3
Chemical addition not otherwise stated (2 pts per reagent/chemical added) |  |  |  |  | 2 to 6
Nitrification via Bioblock or similar small package media filter |  |  |  |  | 1
Nitrification stage (e.g., nitrification tower/trickling filter) |  |  |  |  | 6
Engineered wetlands and/or overland flow treatment - for polishing treatment |  |  |  |  | 4
Tertiary Clarifier |  |  |  |  | 5
Biosolids Stabilization and Solids Handling (Select all applicable items)
Sludge storage lagoon(s) |  |  |  |  | 2
Sludge storage lagoons with aeration |  |  |  |  | 3
Sludge storage tanks with or without gravity settling |  |  |  |  | 2
Sludge drying beds |  |  |  |  | 1
Sludge bags/Geotube bags |  |  |  |  | 3
Aerobic digestion of solids (do not tally for package mechanical activated sludge plants treating an average daily flow of < 15,000 gpd) |  |  |  |  | 6
Anaerobic primary sludge digestion without heating or mixing |  |  |  |  | 5
Anaerobic primary sludge digestion with heating or mixing |  |  |  |  | 7
Anaerobic primary and secondary sludge digesters |  |  |  |  | 10
Sludge digester gas re-use (enter zero if flaring) |  |  |  |  | 4
Sludge DAF thickening |  |  |  |  | 7
Sludge – mechanical thickening in thickener basin(s) |  |  |  |  | 3
Sludge/rotary drum thickener |  |  |  |  | 3
Sludge – belt, screw, plate and frame, or vacuum dewatering |  |  |  |  | 6
Sludge centrifuge dewatering |  |  |  |  | 6
Sludge heat drying (gas/electric), including sludge associated with Class A biosolids process |  |  |  |  | 8
Sludge incineration or microwave drying (Class A) |  |  |  |  | 12
Class B generation/management via aerobic or anaerobic digestion |  |  |  |  | 1
Sludge chemical addition units-class B lime/alkaline stabilization, etc. |  |  |  |  | 2
Sludge chemical addition units (alum, polymer, etc.) not addressed above [add 2 points per location where chemicals are added] |  |  |  |  | 2, 4, 6, etc.
Additional Class A biosolids not otherwise specified (incl thermophilic reactor) |  |  |  |  | 5
Hauling raw sludge to another plant for processing |  |  |  |  | 0
Disposal of dewatered biosolids in a permitted Landfill |  |  |  |  | 0
Land application of Class B biosolids by contractor |  |  |  |  | 1
Land application of Class B biosolids under direction of Utility |  |  |  |  | 4
Sludge composting in windrows |  |  |  |  | 2
Sludge composting in vessel |  |  |  |  | 10
Disinfection (0 point minimum to 10 point maximum) (Select one)
Dry or liquid chlorine disinfection |  |  |  |  | 2
Gas chlorine disinfection |  |  |  |  | 5
Tablet Chlorination |  |  |  |  | 1
Dechlorination system |  |  |  |  | 2
Tablet Dechlorination |  |  |  |  | 1
Peracetic Acid disinfection |  |  |  |  | 4
Ultraviolet disinfection |  |  |  |  | 5
Ozonation disinfection |  |  |  |  | 10
Chlorine Dioxide disinfection |  |  |  |  | 5
Effluent permit requirements for discharge (Select value closest to lowest year-round or seasonal permit limit. If limit is exactly in between two values, choose the lower applicable limit.) Tally all items, as applicable
Minimum of secondary effluent limitation for BOD5 or CBOD5, including limits imposed by an ADEM UIC Permit |  |  |  |  | 0
Minimum of 20 mg/L BOD5 or 17 mg/L CBOD5 |  |  |  |  | 1
Minimum of 10 mg/L BOD5 or 8 mg/L CBOD5 |  |  |  |  | 4
Minimum of 5 mg/L BOD5 or 4 mg/L CBOD5 |  |  |  |  | 6
Percolation pond (one or more) |  |  |  |  | 4
Recycle of effluent for plant use |  |  |  |  | 1
Recycle of effluent for public nonpotable reuse (e.g., irrigation) |  |  |  |  | 4
Land treatment and disposal (surface or subsurface disposal other than percolation pond) |  |  |  |  | 4
HCR-regulated discharge pond |  |  |  |  | 2
Instrumentation (0 point minimum to 6 point maximum) (Select one)
Use of SCADA or similar instrumentation systems to provide data w/ no process operation |  |  |  |  | 0
Use of SCADA or similar instrumentation systems to provide data w/ limited process operation |  |  |  |  | 2
Use of SCADA or similar instrumentation systems to provide data w/ moderate process operation (including remote operation) |  |  |  |  | 4
Use of SCADA or similar instrumentation systems to provide data w/ extensive or total process operation (including remote operation) |  |  |  |  | 6
Laboratory-Operator Control [See Note 2]
Bacteriological testing (0 point minimum to 5 point maximum. Select one)
Lab work done outside the plant |  |  |  |  | 0
Basic coliform or E. coli dilution tube test kit, with or without incubation |  |  |  |  | 2
Use of fermentation tubes, membrane filtration, agar methods, enzyme/fluorescence tests, or any other dilution method for fecal or E. coli definitive/MPN determination |  |  |  |  | 5
Chemical/physical. Select all applicable. Include points for lab analysis related permit to compliance testing and/or Operator control testing)
Lab work done outside the plant |  |  |  |  | 0
Push-button or visual methods for simple tests such as pH, settleable solids, DO, and ORP. Includes basic test strip readings. |  |  |  |  | 3
Additional procedures such as COD, BOD, titrations, MLSS, TSS, volatile solids |  |  |  |  | 5
More advanced determinations such as specific constituents [e.g., Ammonia (2 pts), TKN (2 pts), phosphorus (2 pts), nitrates (1 pt). Total no more than 7 pts.] |  |  |  |  | 1 to 7
Highly Advanced Laboratory-Operator Testing (Select all appicable) [See Note 3]
Lab work done outside the plant |  |  |  |  | 0
Wet chemistry methods such as cyanide or metals testing |  |  |  |  | 7
Highly sophisticated instrumentation such as atomic absorption, gas chromatography |  |  |  |  | 12
|  |  | Points Tally From Above |  |  | 0
|  |  | Classification based on 335-10-1-.06 |  |  | Grade I
Definitions:
- STEP: Septic Tank Effluent Pumping systems in collection system
- STEG: Septic Tank Effluent Gravity systems in collection system
- UIC: Underground Injection Control Permit System
- MPN: Most Probable Number
- SSO: Sanitary Sewer Overflow
Note 1:
Account for I/I, septage, hauled waste, or toxicity only if plant operations are impacted by these conditions. If the operator takes no action to account for these issues, enter 0 points.
Note 2:
The key concept is to account for laboratory analyses performed on-site under the direct supervision of the operator of record or the operator in direct responsible charge. Laboratory testing includes analytical testing for permit compliance as well as diagnostic testing for plant operations, as well as sludge determination testing and SSO testing. For most wastewater plants, anaytical capabilities would include some degree of chemical/physical test procedures. Some plants may also conduct bacteriological testing. The point tally for bacteriological testing is 0 to 5 points. The point tally for chemical/physical testing is 0 to 15 points.
Note 3:
The category includes advanced analysis for permit compliance purposes. Most plants do not conduct highly advance laboratory testing on site. However, for these plants conducting such testing, include those additional points in your plant ranking. The point tally for Highly Advanced Laboratory - operator testing is 0 to 19 points.